Community Design Review Committee – Memorandum

Fire Review

04/14/2025

1st  Review

SBL: 57.22-2-16

33 Union Rd.

Spring Valley, NY, 10977

Dear Applicant,

The following comments were noted during our review of the proposed site development plan(s) sent via email on or about 04/09/2025. And must be addressed or remedied prior to moving your project forward.  As a reminder, escrow balance deficiencies will halt any further review and may delay your project.

- The proposed building is set back from the public way more than 500 feet based on the site plan you submitted and is required to have an approved turnaround as specified in the 2020 Fire Code of New York State Appendix D section D103.  The current proposed turnaround does not meet the minimum specifications set within Figure D103.1.

- The proposed building is in excess of 30 feet high to the eaves and will require Aeiral access as per 2020 Fire Code of New York State Appendix D Section 105.

- Signage will be required as per 2020 Fire Code of New York State for all areas where required by 2020 Fire Code of New York State Appendix D.

- Note location of all fire hydrants, this shall include all “private” current and proposed hydrants on site and those within 500’ of the property entrance.

- Approved engineering must be submitted for access and loading as per 2020 Fire Code of New York State Appendix D section 102.1.

- Indicate location of Fire Department Connection (FDC) for the sprinkler system.

- Indicate location of gas meters and any electrical switch boxes on the site plan.

- Indicate all overhead power lines on or adjacent to property and building.

- Indicate the exact distance from the public way to the proposed building.

If there are no noted deficiencies above, then you may move forward with your project. We reserve the right to adjust this review as needed as per the New York State Uniformed Code, local Village Code, and/or NYS or Federal Law.

Be advised that the transmittal of this document does not guarantee approval upon satisfying the comments within. Furthermore, this document and correlating review does not limit the authority of the Building Inspector, Code Enforcement office, or Fire Inspectors office during the Building Permit application and issuance process. If items are found to be inconsistent with or in violation of the currently adopted NYS Uniformed Code, Local Code, or other applicable laws; it is the property owners’ or representatives’ responsibility to correct, amend, or remove such issues, violations, or inconsistencies.

Adam Mc Carey CCEO, MPM LLC    *   Cc – Mike D. Kauker PP, AICP